Sylomer® SR18

TENDER SPECIFICATION

Manufacturer information

Getzner Werkstoffe GmbH

Herrenau 5

A-6706 Buers

Austria

www.getzner.com

Brand: Sylomer® SR18

Product properties

Material	mixed-cell PUR (polyurethane) elastomer bearing;

volume flexible; spring and damper properties;

free of softeners; good chemical resistance against

oils and fats; good UV- and ozone resistance;

for vibration- and sound isolation

Standard dimensions, on stock	Rolls:	Width	1,500 mm

Length	5,000 mm

Thickness	12.5 mm

25.0 mm

Other dimensions and thicknesses	on request

Temperature resistance	-30° C to +70° C

Flammability 	EN ISO 11925-2	class E

Static load limit	up to 0.018 N/mm²*

Operating load range	up to 0.023 N/mm²*

Dynamic modulus of elasticity

preload of 0.018 N/mm²

at 10 Hz, amplitude ±0.11 mm	E’ ≤ 0.28 N/mm²*

Compression set according to EN ISO 1856

(50 % deformation, 23° C, 70 h,

measurement 30 min after relief)	RVD 30 = < 5 %

Thickness**:	……………………………….	mm

Quantity:	……………………………….	m²

Total:	……………………………….	€

*dependency on form factor, shown values are based on form factor q=3

**dependency on the required comfort of use and the resulting

natural frequency (dynamic stiffness of the material)